## Sheet One
Pressure Drop Calculations
Duct Sections (Each change of size requires a new entry; Only show the sections of the longest run from the wall louver to the farthest bathroom exhaust louver)
Duct Section | Duct Size (in.) | Length (in.) | Flow (cfm) | Friction Loss (in / 100ft) | Duct Pressure Drop (in.) | Use Mcquay Duct Sizer or Ductulator to get the friction loss for each duct section
1 | 18"x22" | 269 | 4400 | 0.175 | 0.47075
Total Duct Pressure Drop (in.) |  |  |  |  | 0.47075
Fittings (Include elbows, tees, reducers, enlargers, and outlets of the longest run only)
Fitting | Belongs to | Minor Loss Coefficient |  | Velocity (ft/s) | Fitting Pressure Drop (in.) | Minor Loss Equation
90 deg bend, sharp | Run 1 | 1.3 |  | 28.5 | 0.2368 | Δpminor_loss = 0.192 x ξ ρ v2 / 2
90 deg bend, sharp |  | 1.3 |  | 28.5 | 0.2368 | ρ = density of air (slugs/ft3) = | 0.002336
Baffle Filters |  | - |  |  | 0.81 | v = velocity of air (ft/s)
Total Fitting Pressure Drop (in.) |  |  |  |  | 1.2836 | ξ = minor loss coefficient
Δpminor_loss = minor loss pressure drop (in.)
Total Pressure Drop (in.) |  |  |  |  | 1.7543
Required Fan External Static Pressure (in.) |  |  |  |  | Min. 2"
Use the link below to get the coefficients of the fittings used
Velocity Calculations | [5 empty] | Minor Loss Coefficients of Different Duct Fittings
Duct Run | Duct Size (in.) | Flow (cfm) | Velocity (fpm)
1 | 18" x 22" | 4400 | 1709
Duct Run 1
#VALUE!