## SB
Service Building- Cooling Load Summary
| AREA DETAILS | [5 empty] | OCCUPANCY |  |  | Ashrae Occupancy |  |  |  | INSIDE CONDITIONS |  | FRESH AIR |  |  |  |  | Exhaust Air |  |  |  | EQUIPMENT LOAD |  |  |  | LIGHTING |  |  | A.C CAPACITY
Category | # | SPACE NUMBER | SPACE |  | AREA | TOTAL Area | By Space as per arch Plans | As per Ashrae | TOTAL | Category | Space Usage | Density | TOTAL | TEMP | RH % | l/s person | l/s / sqm | ACH | L/S | rounded L/S | L/S/Unit | # of Unit | L/S | Rounded L/S | W / sqm | W | KW | Total KW | W/sqm | KW | KW | Total KW | Sensible KW | L/S | E.D.B | E.W.B | L.D.B | L.W.B | L/S / sqm | W / sqm | COOLING UNIT
Prep and Shrouding area | 1 | SB-001 | Washing and Shrouding Room for Decomposed Corpses | غرفة غسيل وتكفين الوفيات المتحللة | 20 | 20 | 2 |  | 2 | Public Assembly Space | Lobbies | #N/A | 0 | 22 | 50 | 0 | 0 | 2 | 33.3333 | 35 |  |  | 39.2157 | 40 | 0 | 0 | 0 | 0 | 10 | 0.2 | 0.2 |  |  | 2850 | 23.3 | 16.5 | 13 | 12.4 | 142.5 | 0 | RTU-01b
Prep and Shrouding area | 2 | SB-002 | Washing and Shrouding Room for Decomposed Corpses | غرفة غسيل وتكفين الوفيات المتحللة | 20 | 20 | 2 |  | 2 | 0 | 0 | #N/A | 0 | 22 | 51 | 0 | 0 | 2 | 33.3333 | 35 |  |  | 39.2157 | 40 | 0 | 2700 | 2.7 | 2.7 | 10 | 0.2 | 0.2 |  |  | 3900 | 23.4 | 16.7 | 13 | 12.4 | 195 | 0 | RTU-01c
Prep and Shrouding area | 3 | SB-003 | Mortuary Refrigirator | ثلاجة الموتي | 43.5 | 43.5 |  |  | 0 | 0 | 0 | #N/A | 0 | 26 | <60 | 0 | 0 | 2 | 72.5 | 75 |  |  | 85.2941 | 90 | 50 | 0 | 2.175 | 2.175 | 10 | 0.435 | 0.435 |  |  | 103 | 24.8 | 8 | 12.5 | 1.7 | 2.3678 | 0 | MSIU-01
mechanical/maintenance room | 4 | SB-004 | Equipment Maintenance Workshop | ورشة صيانة المعدات | 44 | 44 | 2 |  | 2 | 0 | 0 | #N/A | 0 | 22 | <60 | 0 | 0.3 |  | 13.2 | 15 |  |  | 11.22 | 10 | 0 | 250 | 0.25 | 0.25 | 10 | 0.44 | 0.44 |  |  | 70 | 22.8 | 16.9 | 13.6 | 13.1 | 1.5909 | 0 | VRF-01
Laundry Room | 5 | SB-005 | Sheet Washing Room | غرفة غسيل الشراشف | 24 | 24 |  |  | 0 | 0 | 0 | #N/A | 0 | 22 | <60 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 250 | 0.25 | 0.25 | 10 | 0.24 | 0.24 |  |  | 70 | 22.8 | 16.9 | 13.6 | 13.1 | 2.9167 | 0 | VRF-01
bathroom | 7 | SB-006 | Excavator Workers Toilet | دورة مياه عمال الحفر | 38.5 | 38.5 | 6 |  | 6 | 0 | 0 | #N/A | 0 | 26 | <60 | 0 | 0 |  | 127.5 | 130 | 25 | 6 | 150 | 150 | 50 | 0 | 1.925 | 1.925 | 10 | 0.385 | 0.385 |  |  | 19 | 24 | 7.7 | 11 | 0.8 | 0.49351 | 0 | MSIU-01
Waiting Area | 8 | SB-007 | Excavator Workers Resting Area | استراحة عمال الحفر | 38.5 | 38.5 | 17 |  | 17 | 0 | 0 | #N/A | 0 | 22 | <60 | 3.8 | 0.3 |  | 76.15 | 80 |  |  | 64.7275 | 65 | 0 | 250 | 0.25 | 0.25 | 10 | 0.385 | 0.385 |  |  | 71 | 22.7 | 16.8 | 13.3 | 12.8 | 1.8442 | 0 | VRF-01
Storage | 9 | SB-008 | Main Warehouse for Processing Materials | مستودع رئيسي لمواد التجهيز | 38.5 | 38.5 |  |  | 0 | 0 | 0 | #N/A | 0 | 22 | <60 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 2000 | 2 | 2 | 10 | 0.385 | 0.385 |  |  | 216 | 22.5 | 10 | 13 | 5.6 | 5.6104 | 0 | VRF-02
Storage | 10 | SB-009 | Al-Baqi' Equipement Warehouse | مخزن معدات البقيع | 48 | 48 |  |  | 0 | 0 | 0 | #N/A | 0 | 22 | <60 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.48 | 0.48 |  |  | 103 | 22.7 | 16.9 | 13.1 | 12.5 | 2.1458 | 0 | VRF-02
Storage | 11 | SB-010 | Water Bottle Cooling Room | غرفة تبريد عبوات مياه الشرب | 51 | 51 |  |  | 0 | 0 | 0 | #N/A | 0 | 22 | <60 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 500 | 0.5 | 0.5 | 10 | 0.51 | 0.51 |  |  | 69 | 22.9 | 11.8 | 13.4 | 7.6 | 1.3529 | 0 | VRF-02
| Totals and Averages |  |  |  |  | #REF! | #REF! |  |  | #REF! |  |  |  | - |  | #REF! | [8 empty] | 10 KW |  |  |  | 4 KW |  |  | 0 | 0 | 7471 | - | - | - | - | #REF! | #REF! | -

## MB
Cemetary Main Building- Cooling Load Summary
| AREA DETAILS | [6 empty] | OCCUPANCY |  |  | Ashrae Occupancy |  |  |  | INSIDE CONDITIONS |  | FRESH AIR |  |  |  |  | Transfer | EXHAUST AIR |  |  |  | Exhaust | Pressurization | Space Pressurization | ACH VALUE | ACH BETWEEN 03 AND 0..8 | EQUIPMENT LOAD |  |  |  | LIGHTING |  |  | A.C CAPACITY
| 2606.56 | [15 empty] | 1370 | [5 empty] | -815
Category | # |  | SPACE NUMBER | SPACE |  | AREA | TOTAL Area | By Space as per arch Plans | As per Ashrae | TOTAL | Category | Space Usage | Density | TOTAL | TEMP | RH % | l/s person | l/s / sqm | ACH | L/S | Rounded L/S |  | L/S/Unit or meter | # of Unit | L/S | Rounded L/S | [5 empty] | W / sqm | W | KW | Total KW | W/sqm | KW | KW | Total KW | Sensible KW | Quantity | Sensible Cooling Load per FCU | Selected Sensible Load | Supply L/S | Return L/S | E.D.B | E.W.B | L.D.B | L.W.B | L/S / sqm | Btu/hr/ sqm | COOLING UNIT | FCU SELECTION
Storage | 1 | Group 6 | GF-001 | Sub-Store for Supplies | خزن فرعي لمستلزمات التجهيز | 16 | 16 | 1 |  | 1 | 0 | 0 | 2 | 0 | 22 | 50 | 0 | 0 |  | 0 | 11 |  |  |  | 0 | 25 | -15 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.16 | 0.16 |  |  | 1 | 0 | 2.3 | 158 | 147 |  |  |  |  | 9.875 | 488.75 | VRV-GF-01 | FXSQ32A
Trash | 2 | Group 6 | GF-002 | Garbage Room | غرفة نفايات | 12.5 | 12.5 | 1 |  | 1 | 0 | 0 | 0 | 0 | 22 | 51 | 0 | 0 |  |  | 60 |  |  |  | 65 | 65 | -65 |  | Negative | 0.48 | TRUE |  |  |  |  | 0 | 0 | 0 |  |  | 1 | 0 | 1 | 150 | 90 |  |  |  |  | 12 | 272 | VRV-GF-01 | FXSQ20A
Laundry Room | 3 | Group 6 | GF-003 | Sheet Washing Room | غرفة غسيل الملاءات | 11.2 | 11.2 | 1 |  | 1 | 0 | 0 | 0 | 0 | 26 | <60 | 0 | 0 |  | 0 | 50 |  |  |  | 0 | 55 | -55 |  | Negative | 0.54 | TRUE |  |  |  |  | 10 | 0.112 | 0.112 |  |  | 1 | 0 | 5.9 | 533 | 483 |  |  |  |  | 47.5893 | 1791.0714 | VRV-GF-01 | FXSQ100A
Storage | 4 | Group 6 | GF-004 | Cleaning Supplies Storage | مخزن مستلزمات تنظيف | 6 | 6 | 1 |  | 1 | 0 | 0 | 2 | 0 | 22 | <60 | 0 | 0 |  | 0 | 12 |  |  |  | 10 | 25 | -15 |  | Negative | 0.6 | TRUE |  |  |  |  | 10 | 0.06 | 0.06 |  |  | 1 | 0 | 0 | 150 | 138 |  |  |  |  | 25 | 0 | VRV-GF-01 | With Corridor GF-016
Storage | 5 | Group 6 | GF-005 | Sanitizing Room | غرفة تعقيم | 6 | 6 | 1 |  | 1 | 0 | 0 | 2 | 0 | 22 | <60 | 0 | 0 |  | 10 | 12 |  |  |  | 0 | 25 | -15 |  | Negative | 0.6 | TRUE |  |  |  |  | 10 | 0.06 | 0.06 |  |  | 1 | 0 | 0 | 150 | 138 |  |  |  |  | 25 | 0 | VRV-GF-01 | With Corridor GF-016
Storage | 6 | Group 6 | GF-006 | Preparation Supplies Storage | مخزن مستلزمات اعداد | 12.5 | 12.5 | 1 |  | 1 | 0 | 0 | 2 | 0 | 22 | <60 | 0 | 0 |  | 0 | 10 |  |  |  | 10 | 25 | -15 |  | Negative | 0.48 | TRUE |  |  |  |  | 10 | 0.125 | 0.125 |  |  | 1 | 0 | 0 | 150 | 140 |  |  |  |  | 12 | 0 | VRV-GF-01 | With Corridor GF-016
Prep and Shrouding area | 7 | Group 6 | GF-007 | Women's Viewing Room | غرفة مشاهدة نساء | 20 | 20 | 12 |  | 12 | 0 | 0 | 0 | 0 | 26 | <60 | 0 | 0 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 1.7 | 150 | 115 |  |  |  |  | 7.5 | 289 | VRV-GF-01 | FXSQ25A
Prep and Shrouding area | 8 | Group 6 | GF-008 | Women's Viewing Room | غرفة مشاهدة نساء | 20 | 20 | 12 |  | 12 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 1.7 | 150 | 115 |  |  |  |  | 7.5 | 289 | VRV-GF-01 | FXSQ25A
Prep and Shrouding area | 9 | Group 6 | GF-009 | Women's Viewing Room | غرفة مشاهدة نساء | 20 | 20 | 12 |  | 12 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 1.7 | 150 | 115 |  |  |  |  | 7.5 | 289 | VRV-GF-01 | FXSQ25A
bathroom | 10 | Group 6 | GF-010 | Women's Rest Room | دورة مياه نساء | 21 | 21 | 4 |  | 0 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 |  | 106.25 | 0 | 115 | 25 | 5 | 125 | 125 | -125 |  | Negative | 0.57 | TRUE |  |  |  |  | 10 | 0.21 | 0.21 |  |  | 1 | 0 | 2.8 | 250 | 250 |  |  |  |  | 11.9048 | 453.3333 | VRV-GF-01 | with GF-016 Waiting Room
Storage | 11 | Group 6 | GF-011 | Cold Room | غرفة تبريد | 27 | 27 | 1 |  | 1 | 0 | 0 | 2 | 0 | 22 | <60 | 0 | 0 | 2 | 45 | 45 |  |  |  | 52.9412 | 55 | -55 |  | Negative | 0.44 | TRUE |  |  |  |  | 10 | 0.27 | 0.27 |  |  | 1 | 0 | 1.9 | 158 | 113 |  |  |  |  | 5.8519 | 239.2593 | VRV-GF-01 | FXSQ32A
Prep and Shrouding area | 12 | Group 6 | GF-012 | Preparation and Shrouding Room | غرفة تجهيز وتكفين | 20 | 20 | 2 |  | 2 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 2.4 | 158 | 123 |  |  |  |  | 7.9 | 408 | VRV-GF-01 | FXSQ32A
Prep and Shrouding area | 13 | Group 6 | GF-013 | Preparation and Shrouding Room | غرفة تجهيز وتكفين | 20 | 20 | 2 |  | 2 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 2.4 | 158 | 123 |  |  |  |  | 7.9 | 408 | VRV-GF-01 | FXSQ32A
Prep and Shrouding area | 14 | Group 6 | GF-014 | Preparation and Shrouding Room | غرفة تجهيز وتكفين | 20 | 20 | 2 |  | 2 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 2.4 | 158 | 123 |  |  |  |  | 7.9 | 408 | VRV-GF-01 | FXSQ32A
Prep and Shrouding area | 15 | Group 6 | GF-015 | Preparation and Shrouding Room | غرفة تجهيز وتكفين | 20 | 20 | 2 |  | 2 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 2.4 | 158 | 123 |  |  |  |  | 7.9 | 408 | VRV-GF-01 | FXSQ32A
Waiting Area | 16 | Group 6 | GF-016 | Waiting Room | صالة انتظار | 98 | 98 | 9 |  | 9 | 0 | 0 | 50 | 0 | 22 | <60 | 3.8 | 0.3 |  | 63.6 | 200 | -115 |  |  | 170 |  | 0 |  | Positive | 1.04 | FALSE |  |  |  |  | 10 | 0.98 | 0.98 |  |  | 2 | 0 | 3.9 | 350 | 150 |  |  |  |  | 3.5714 | 135.3061 | VRV-GF-Common Areas | FXSQ63A
Office | 17 | Group 10 | GF-017 | First Aid Medical Care Room | غرفة رعاية طبية اسعافات اولية | 12 | 12 | 2 |  | 2 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 8.6 | 30 |  |  |  | 25.5 | 26 |  | -25 | Positive | 0.5 | TRUE |  |  |  |  | 10 | 0.12 | 0.12 |  |  | 1 | 0 | 2.1 | 158 | 128 |  |  |  |  | 13.1667 | 595 | VRV-GF-01 | FXSQ32A
Reception | 18 | Group 10 | GF-018 | Reception | مكتب استقبال | 99.04 | 99.04 | 30 |  | 30 | 0 | 0 | 30 | 0 | 22 | <60 | 2.5 | 0.3 |  | 104.712 | 105 |  |  |  | 89.25 | 90 |  | -70 | Positive | 0.42 | TRUE |  |  |  |  | 10 | 0.9904 | 0.9904 |  |  | 1 | 0 | 6.8 | 533 | 428 |  |  |  |  | 5.3817 | 233.441 | VRV-GF-Common Areas | FXSQ100A
Waiting Area | 19 | Group 10 | GF-018-A | Family Waiting Room | صالة انتظار عائلية | 31.6 | 31.6 | 10 |  | 10 | 0 | 0 | 50 | 0 | 22 | <60 | 3.8 | 0.3 |  | 47.48 | 50 |  |  |  | 42.5 | 43 |  | -40 | Positive | 0.38 | TRUE |  |  |  |  | 10 | 0.316 | 0.316 |  |  | 1 | 0 | 4.1 | 350 | 300 |  |  |  |  | 11.0759 | 441.1392 | VRV-GF-Common Areas | FXSQ63A
Waiting Area | 20 | Group 10 | GF-018-B | Family Waiting Room | صالة انتظار عائلية | 31.6 | 31.6 | 17 |  | 17 | 0 | 0 | 50 | 0 | 22 | <60 | 3.8 | 0.3 |  | 74.08 | 75 |  |  |  | 63.75 | 75 |  | -65 | Positive | 0.38 | TRUE |  |  |  |  | 10 | 0.316 | 0.316 |  |  | 1 | 0 | 3.8 | 350 | 275 |  |  |  |  | 11.0759 | 408.8608 | VRV-GF-Common Areas | FXSQ63A
Office | 21 | Group 10 | GF-018-C | Security Office | مكتب امن | 9.52 | 9.52 | 1 |  | 1 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 5.356 | 10 |  |  |  | 8.5 | 9 |  | -7 | Positive | 0.38 | TRUE |  |  |  |  | 10 | 0.0952 | 0.0952 |  |  | 1 | 0 | 5.6 | 383 | 373 |  |  |  |  | 40.2311 | 2000 | VRV-GF-Common Areas | FXSQ80A
Corridor | 22 | Group 8 | GF-018-D | Corridor |  | 84 | 84 | 0 |  | 0 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0.3 |  | 25.2 | 50 |  |  |  | 42.5 |  | 0 |  | Positive | 0.71 | TRUE |  |  |  |  | 10 | 0.84 | 0.84 |  |  | 1 | 0 | 4.2 | 350 | 300 |  |  |  |  | 4.1667 | 170 | VRV-GF-Common Areas | FXSQ63A
Corridor | 23 | Group 9 | GF-018-E | Corridor |  | 80 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0.3 |  | 24 | 310 | -260 |  |  |  | 0 | 0 |  | Positive | 0.75 | TRUE |  |  |  |  | 10 | 0.8 | 0.8 |  |  | 1 | 0 | 2.3 | 158 | -152 |  |  |  |  | 1.975 | 97.75 | VRV-GF-Common Areas | FXSQ32A
Office | 24 | Group 8 | GF-019 | Corporate Social Responsibility Office | مكتب مسؤولية مجتمعية | 19.2 | 19.2 | 3 |  | 3 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 13.26 | 15 | -10 |  |  | 12.75 |  | 0 |  | Positive | 0.31 | TRUE |  |  |  |  | 10 | 0.192 | 0.192 |  |  | 1 | 0 | 2.6 | 250 | 235 |  |  |  |  | 13.0208 | 460.4167 | VRV-GF-01 | FXSQ40A
mechanical/maintenance room | 25 | Group 8 | GF-020 | Mechanical Room | غرفة خدمات ميكانيكية | 13.44 | 13.44 | 1 |  | 1 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0.3 |  | 4.032 |  | 20 |  |  | 0 | 25 | -25 |  | Negative | 0.45 | TRUE |  |  |  |  | 10 | 0.1344 | 0.1344 |  |  | 1 | 0 | 1.5 | 150 | 150 |  |  |  |  | 11.1607 | 379.4643 | VRV-GF-01 | FXSQ20A
Office | 26 | Group 8 | GF-021 | Operational Services Room | غرفة خدمات تشغيلية | 13.92 | 13.92 | 1 |  | 1 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 6.676 | 10 | -5 |  |  | 8.5 |  | 0 |  | Positive | 0.43 | TRUE |  |  |  |  | 10 | 0.1392 | 0.1392 |  |  | 1 | 0 | 1.6 | 150 | 140 |  |  |  |  | 10.7759 | 390.8046 | VRV-GF-01 | FXSQ25A
Storage | 27 | Group 8 | GF-022 | Water Bottle Storage Room | غرفة تخزين عبوات مياه الشرب | 18.24 | 18.24 | 1 |  | 1 | 0 | 0 | 2 | 0 | 22 | <60 | 0 | 0 |  | 0 |  | 20 |  |  | 0 | 25 | -25 |  | Negative | 0.33 | TRUE |  |  |  |  | 10 | 0.1824 | 0.1824 |  |  | 1 | 0 | 1.9 | 158 | 158 |  |  |  |  | 8.6623 | 354.1667 | VRV-GF-01 | FXSQ32A
Office | 28 | Group 8 | GF-023 | Customer Service Lounge | استراحة خدمة العملاء | 44.4 | 44.4 | 17 |  | 17 | 0 | 1 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 55.82 | 60 | -20 |  |  | 51 |  | -25 |  | Positive | 0.41 | TRUE |  |  |  |  | 10 | 0.444 | 0.444 |  |  | 1 | 0 | 5.8 | 383 | 323 |  |  |  |  | 8.6261 | 444.1441 | VRV-GF-01 | FXSQ80A
mechanical/maintenance room | 29 | Group 8 | GF-024 | Maintenance Room | غرفة صيانة | 21.78 | 21.78 | 0 |  | 0 | 0 | 1 | 0 | 0 | 22 | <60 | 0 | 0.3 |  | 6.534 |  | 15 |  |  | 0 | 25 | -25 |  | Negative | 0.55 | TRUE |  |  |  |  | 10 | 0.2178 | 0.2178 |  |  | 1 | 0 | 2.8 | 250 | 250 |  |  |  |  | 11.4784 | 437.0983 | VRV-GF-01 | FXSQ40A
bathroom | 30 |  | GF-025 | Women's Rest Room | دورة مياه نساء | 30.09 | 30.09 | 5 |  | 5 | 0 | 8 | 0 | 0 | 22 | <60 | 0 | 0 |  | 0 | 0 |  | 25 | 6 | 150 | 150 | -150 |  | Negative | 5.98 | FALSE |  |  |  |  | 10 | 0.3009 | 0.3009 |  |  | 1 | 0 | 2.8 | 250 | 250 | [5 empty] | 316.3842 | Served By RTU-01
Ablution | 31 |  | GF-026 | Ablution | موضى | 14 | 14 | 6 |  | 6 | 0 | 1 | 0 | 0 | 22 | <60 | 0 | 0 |  | 15.3 | 20 |  | 1.25 |  | 17.5 | 18 | -18 |  | Positive | 0.17 | FALSE |  |  |  |  | 10 | 0.14 | 0.14 |  |  | 1 | 0 | 5.6 | 383 | 363 | [5 empty] | 1360 | Served By RTU-01
Prayer Room | 32 |  | GF-027 | Prayer Room | مصلى | 35.4 | 35.4 | 25 |  | 25 | 0 | 3 | 120 | 0 | 22 | <60 | 2.5 | 0.3 |  | 73.12 | 75 |  |  |  | 63.75 | 64 | -64 |  | Positive | 0.37 | TRUE |  |  |  |  | 10 | 0.354 | 0.354 |  |  | 1 | 0 | 11.9 | 0 | -75 | [5 empty] | 1142.9379 | Served By RTU-01
Cafeteria | 33 |  | GF-028 | Cafeteria | كافتيريا | 290.1 | 290.1 | 128 |  | 128 | 0 | 1 | 100 | 0 | 22 | <60 | 3.8 | 0.9 |  | 747.49 | 750 |  |  |  | 637.5 | 638 | -638 |  | Positive | 0.46 | TRUE |  |  |  |  | 10 | 2.901 | 2.901 |  |  | 1 | 0 | 1.5 | 150 | -600 | [5 empty] | 17.5801 | Served By RTU-01
Office | 34 | Group 10 | GF-029 | Government Security Office | مكتب امن حكومي | 13.6 | 13.6 | 3 |  | 3 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 11.58 | 15 |  |  |  | 12.75 | 13 |  | -10 | Positive | 0.44 | TRUE |  |  |  |  | 10 | 0.136 | 0.136 |  |  | 1 | 0 | 3.1 | 253 | 238 |  |  |  |  | 18.6029 | 775 | VRV-GF-02 | FXSQ50A
Cafeteria | 35 |  | GF-030 | Cafeteria | كافتيريا | 380.16 | 380.16 | 192 |  | 192 | 0 | 0 | 100 | 0 | 22 | <60 | 3.8 | 0.9 |  | 1071.744 | 1075 |  |  |  | 913.75 | 914 | -914 |  | Positive | 0.51 | TRUE |  |  |  |  | 10 | 3.8016 | 3.8016 |  |  | 1 | 0 | 1.5 | 150 | -925 |  |  |  |  | 0.39457 | 13.4154 | Served By RTU-02
Prayer Room | 36 | Group 9 | GF-031 | Prayer Room | مصلى | 61.36 | 61.36 | 46 |  | 46 | 0 | 3 | 120 | 0 | 22 | <60 | 2.5 | 0.3 |  | 133.408 | 135 |  |  |  | 114.75 |  | -115 |  | Positive | 0.39 | TRUE |  |  |  |  | 10 | 0.6136 | 0.6136 |  |  | 1 | 0 | 7.9 | 600 | 465 |  |  |  |  | 9.7784 | 437.7445 | VRV-GF-02 | FXSQ125A
bathroom | 37 | Group 9 | GF-032 | Men's Rest Room | دورة مياه رجال | 70.635 | 70.635 | 10 |  | 10 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 |  | 255 |  | 270 | 25 | 12 | 300 | 300 | -300 |  | Negative | 0.51 | TRUE |  |  |  |  | 10 | 0.70635 | 0.70635 |  |  | 1 | 0 | 5.9 | 533 | 533 |  |  |  |  | 7.5458 | 283.9952 | VRV-GF-02 | FXSQ100A
Ablution | 38 | Group 9 | GF-033 | Ablution | موضى | 15.36 | 15.36 | 6 |  | 6 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 |  | 17 |  | 15 | 1.25 |  | 19.2 | 20 | -20 |  | Negative | 0.39 | TRUE |  |  |  |  | 10 | 0.1536 | 0.1536 |  |  | 1 | 0 | 1.7 | 150 | 150 |  |  |  |  | 9.7656 | 376.3021 | VRV-GF-02 | FXSQ25A
Office | 39 | Group 9 | GF-034 | Shift Supervisor Office | مكتب مشرف الوردية | 20.16 | 20.16 | 3 |  | 3 | 0 | 0 | 5 | 0 | 22 | 49 | 2.5 | 0.3 |  | 13.548 | 15 | -10 |  |  | 12.75 |  | 0 |  | Positive | 0.3 | TRUE |  |  |  |  | 10 | 0.2016 | 0.2016 |  |  | 1 | 0 | 2.5 | 250 | 235 |  |  |  |  | 12.4008 | 421.627 | VRV-GF-02 | FXSQ40A
Office | 40 | Group 9 | GF-035 | Shift Supervisor Office | مكتب مشرف الوردية | 19.2 | 19.2 | 3 |  | 3 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 13.26 | 15 | -10 |  |  | 12.75 |  | 0 |  | Positive | 0.31 | TRUE |  |  |  |  | 10 | 0.192 | 0.192 |  |  | 1 | 0 | 2.4 | 158 | 143 |  |  |  |  | 8.2292 | 425 | VRV-GF-02 | FXSQ32A
Cafeteria | 41 | Group 9 | GF-036 | Cafeteria | كافتيريا | 14.4 | 14.4 | 3 |  | 3 | 0 | 0 | 100 | 0 | 22 | 59 | 3.8 | 0.9 |  | 24.36 | 25 |  |  |  | 29.4118 | 30 | -30 |  | Negative | 0.42 | TRUE |  |  |  |  | 10 | 0.144 | 0.144 |  |  | 1 | 0 | 2.1 | 158 | 133 |  |  |  |  | 10.9722 | 495.8333 | VRV-GF-02 | FXSQ32A
Office | 42 | Group 9 | GF-037 | Burial Certificate issuance Office | مكتب اصدار شهادة الدفن | 21.6 | 21.6 | 3 |  | 3 |  |  | 5 | 0 | 26 | <60 | 2.5 | 0.3 |  | 13.98 | 15 | -5 |  |  | 12.75 |  | 0 |  | Positive | 0.56 | TRUE |  |  |  |  | 10 | 0.216 | 0.216 |  |  | 1 | 0 | 2.7 | 250 | 235 |  |  |  |  | 11.5741 | 425 | VRV-GF-02 | FXSQ40A
Office | 43 | Group 10 | GF-038 | First Aid Medical Care Room | غرفة رعاية طبية اسعافات اولية | 12 | 12 | 2 |  | 2 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 8.6 | 30 |  |  |  | 25.5 | 15 |  | -25 | Positive | 0.5 | TRUE |  |  |  |  | 10 | 0.12 | 0.12 |  |  | 1 | 0 | 1.7 | 150 | 120 |  |  |  |  | 12.5 | 481.6667 | VRV-GF-02 | FXSQ25A
Waiting Area | 44 | Group 7 | GF-039 | Waiting Room | صالة انتظار | 108.8 | 108.8 | 9 |  | 9 | 0 | 0 | 50 | 0 | 22 | <60 | 3.8 | 0.3 |  | 66.84 | 150 | -84 |  |  | 127.5 |  | 0 |  | Positive | 0.73 | TRUE |  |  |  |  | 10 | 1.088 | 1.088 |  |  | 1 | 0 | 6.5 | 533 | 383 |  |  |  |  | 4.8989 | 203.125 | VRV-GF-Common Areas | FXSQ100A
Prep and Shrouding area | 45 | Group 7 | GF-040 | Preparation and Shrouding Room | غرفة تجهيز وتكفين | 20 | 20 | 2 |  | 2 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 2.4 | 158 | 123 |  |  |  |  | 7.9 | 408 | VRV-GF-02 | FXSQ32A
Prep and Shrouding area | 46 | Group 7 | GF-041 | Preparation and Shrouding Room | غرفة تجهيز وتكفين | 20 | 20 | 2 |  | 2 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 2.4 | 158 | 123 |  |  |  |  | 7.9 | 408 | VRV-GF-02 | FXSQ32A
Prep and Shrouding area | 47 | Group 7 | GF-042 | Preparation and Shrouding Room | غرفة تجهيز وتكفين | 20 | 20 | 2 |  | 2 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 2.4 | 158 | 123 |  |  |  |  | 7.9 | 408 | VRV-GF-02 | FXSQ32A
Prep and Shrouding area | 48 | Group 7 | GF-043 | Preparation and Shrouding Room | غرفة تجهيز وتكفين | 20 | 20 | 2 |  | 2 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 2.4 | 158 | 123 |  |  |  |  | 7.9 | 408 | VRV-GF-02 | FXSQ32A
Prep and Shrouding area | 49 | Group 7 | GF-044 | Preparation and Shrouding Room | غرفة تجهيز وتكفين | 20 | 20 | 2 |  | 2 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 2.4 | 158 | 123 |  |  |  |  | 7.9 | 408 | VRV-GF-02 | FXSQ32A
Storage | 50 | Group 7 | GF-045 | Cold Room | غرفة تبريد | 27.5 | 27.5 | 0 |  | 0 | 0 | 0 | 2 | 0 | 22 | <60 | 0 | 0 | 2 | 45.8333 | 45 |  |  |  | 53.9216 | 55 | -55 |  | Negative | 0.44 | TRUE |  |  |  |  | 10 | 0.275 | 0.275 |  |  | 1 | 0 | 1.9 | 158 | 113 |  |  |  |  | 5.7455 | 234.9091 | VRV-GF-02 | FXSQ32A
bathroom | 51 | Group 7 | GF-046 | Men's Rest Room | دورة مياه رجال | 21.5 | 21.5 | 4 |  | 4 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 |  | 127.5 | 140 |  | 25 | 6 | 150 | 150 | -150 |  | Negative | 0.56 | TRUE |  |  |  |  | 10 | 0.215 | 0.215 |  |  | 1 | 0 | 2.3 | 158 | 18 |  |  |  |  | 7.3488 | 363.7209 | VRV-GF-02 | FXSQ32A
Storage | 52 | Group 7 | GF-047 | Sub-Store for Supplies | خزن فرعي لمستلزمات التجهيز | 16 | 16 | 1 |  | 1 | 0 | 0 | 2 | 0 | 22 | 50 | 0 | 0 |  | 0 |  | 20 |  |  | 0 | 25 | -25 |  | Negative | 0.38 | TRUE |  |  |  |  | 10 | 0.16 | 0.16 |  |  | 1 | 0 | 1.9 | 158 | 158 |  |  |  |  | 9.875 | 403.75 | VRV-GF-02 | FXSQ32A
Trash | 53 | Group 7 | GF-048 | Garbage Room | غرفة نفايات | 12.5 | 12.5 | 1 |  | 1 | 0 | 0 | 0 | 0 | 22 | 51 | 0 | 0 |  | 55.25 | 58 |  | 5 |  | 62.5 | 65 | -65 |  | Negative | 0.67 | TRUE |  |  |  |  | 0 | 0 | 0 |  |  | 1 | 0 | 1.1 | 150 | 92 |  |  |  |  | 12 | 299.2 | VRV-GF-02 | FXSQ20A
Laundry Room | 54 | Group 7 | GF-049 | Sheet Washing Room | غرفة غسيل الملاءات | 11.2 | 11.2 | 1 |  | 1 | 0 | 0 | 0 | 0 | 26 | <60 | 0 | 0 |  | 0 | 50 |  |  |  | 0 | 55 | -55 |  | Negative | 0.54 | TRUE |  |  |  |  | 10 | 0.112 | 0.112 |  |  | 1 | 0 | 6.1 | 533 | 483 |  |  |  |  | 47.5893 | 1851.7857 | VRV-GF-02 | FXSQ100A
Storage | 55 | Group 7 | GF-050 | Cleaning Supplies Storage | مخزن مستلزمات تنظيف | 6 | 6 | 1 |  | 1 | 0 | 0 | 2 | 0 | 22 | <60 | 0 | 0 |  | 0 |  | 22 |  |  | 0 | 25 | -25 |  | Negative | 0.6 | TRUE |  |  |  |  | 10 | 0.06 | 0.06 |  |  | 1 | 0 | 0 | 150 | 150 |  |  |  |  | 25 | 0 | VRV-GF-02 | FXSQ20A
Storage | 56 | Group 7 | GF-051 | Sanitizing Room | غرفة تعقيم | 6 | 6 | 1 |  | 1 | 0 | 0 | 2 | 0 | 22 | <60 | 0 | 0 |  | 0 |  | 22 |  |  | 0 | 25 | -25 |  | Negative | 0.6 | TRUE |  |  |  |  | 10 | 0.06 | 0.06 |  |  | 1 | 0 | 0 | 150 | 150 |  |  |  |  | 25 | 0 | VRV-GF-02 | FXSQ20A
Storage | 57 | Group 7 | GF-052 | Preparation Supplies Storage | مخزن مستلزمات اعداد | 13.5 | 13.5 | 1 |  | 1 | 0 | 0 | 2 | 0 | 22 | <60 | 0 | 0 |  | 0 |  | 20 |  |  | 0 | 25 | -25 |  | Negative | 0.44 | TRUE |  |  |  |  | 10 | 0.135 | 0.135 |  |  | 1 | 0 | 0 | 150 | 150 |  |  |  |  | 11.1111 | 0 | VRV-GF-02 | FXSQ20A
Meeting room | 58 | Group 7 | GF-053 | Men's Viewing Room | غرفة مشاهدة رجال | 20 | 20 | 12 |  | 12 | 0 | 0 | 50 | 0 | 26 | <60 | 2.5 | 0.3 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 1.7 | 150 | 115 |  |  |  |  | 7.5 | 289 | VRV-GF-02 | FXSQ25A
Meeting room | 59 | Group 7 | GF-054 | Men's Viewing Room | غرفة مشاهدة رجال | 20 | 20 | 12 |  | 12 | 0 | 0 | 50 | 0 | 22 | <60 | 2.5 | 0.3 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 1.7 | 150 | 115 |  |  |  |  | 7.5 | 289 | VRV-GF-02 | FXSQ25A
Meeting room | 60 | Group 7 | GF-055 | Men's Viewing Room | غرفة مشاهدة رجال | 20 | 20 | 12 |  | 12 | 0 | 0 | 50 | 0 | 22 | <60 | 2.5 | 0.3 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 1.7 | 150 | 115 |  |  |  |  | 7.5 | 289 | VRV-GF-02 | FXSQ25A
Meeting room | 61 | Group 7 | GF-056 | Men's Viewing Room | غرفة مشاهدة رجال | 20 | 20 | 12 |  | 12 | 0 | 0 | 50 | 0 | 22 | <60 | 2.5 | 0.3 | 2 | 33.3333 | 35 |  |  |  | 39.2157 | 40 | -40 |  | Negative | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 1.7 | 150 | 115 |  |  |  |  | 7.5 | 289 | VRV-GF-02 | FXSQ25A
Office | 62 | Group 10 | GF-057 | Security Office | مكتب امن | 9.5 | 9.5 | 1 |  | 1 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 5.35 | 10 |  |  |  | 8.5 | 9 |  | -7 | Positive | 0.38 | TRUE |  |  |  |  | 10 | 0.095 | 0.095 |  |  | 1 | 0 | 2.1 | 158 | 148 |  |  |  |  | 16.6316 | 751.5789 | VRV-GF-02 | FXSQ32A
Office | 63 | Group 10 | GF-058 | Customer Service | خدمة العملاء | 11.125 | 11.125 | 1 |  | 1 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 5.8375 | 10 |  |  |  | 8.5 | 9 |  | -7 | Positive | 0.32 | TRUE |  |  |  |  | 10 | 0.11125 | 0.11125 |  |  | 1 | 0 | 2.4 | 158 | 148 |  |  |  |  | 14.2022 | 733.4831 | VRV-GF-01 | FXSQ32A
Office | 64 | Group 10 | GF-059 | Customer Service Office | مكتب خدمة عملاء | 36.9 | 36.9 | 14 |  | 14 | 0 | 0 | 5 | 0 | 26 | <60 | 2.5 | 0.3 |  | 46.07 | 50 |  |  |  | 42.5 | 43 |  | -40 | Positive | 0.33 | TRUE |  |  |  |  | 10 | 0.369 | 0.369 |  |  | 1 | 0 | 2.5 | 250 | 200 |  |  |  |  | 6.7751 | 230.3523 | VRV-GF-01 | FXSQ40A
Office | 65 | Group 10 | GF-060 | Men Preparation Staff | عمالة التجهيز رجال | 17 | 17 | 8 |  | 8 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 25.1 | 30 |  |  |  | 25.5 | 26 |  | -25 | Positive | 0.35 | TRUE |  |  |  |  | 10 | 0.17 | 0.17 |  |  | 1 | 0 | 1.2 | 150 | 120 |  |  |  |  | 8.8235 | 240 | VRV-GF-01 | FXSQ20A
Office | 66 | Group 10 | GF-061 | Women Preparation Staff | عمالة التجهيز نساء | 10.2 | 10.2 | 4 |  | 4 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 13.06 | 15 |  |  |  | 12.75 | 13 |  | -10 | Positive | 0.59 | TRUE |  |  |  |  | 10 | 0.102 | 0.102 |  |  | 1 | 0 | 0.8 | 150 | 135 |  |  |  |  | 14.7059 | 266.6667 | VRV-GF-01 | FXSQ20A
Office | 67 | Group 10 | GF-062 | Security Room | غرفة امن | 12.15 | 12.15 | 1 |  | 1 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 6.145 | 10 |  |  |  | 8.5 | 9 |  | -7 | Positive | 0.3 | TRUE |  |  |  |  | 10 | 0.1215 | 0.1215 |  |  | 1 | 0 | 0.9 | 150 | 140 |  |  |  |  | 12.3457 | 251.8519 | VRV-GF-01 | FXSQ20A
Office | 68 | Group 10 | GF-063 | Security Room | غرفة امن | 12.15 | 12.15 | 1 |  | 1 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 6.145 | 10 |  |  |  | 8.5 | 9 |  | -7 | Positive | 0.3 | TRUE |  |  |  |  | 10 | 0.1215 | 0.1215 |  |  | 1 | 0 | 0.9 | 150 | 140 |  |  |  |  | 12.3457 | 251.8519 | VRV-GF-01 | FXSQ20A
Lobbies | 69 | Group 10 | GF-064 | Lobby |  | 67.5 | 67.5 | 5 |  | 5 | 0 | 0 | 10 | 0 | 22 | <60 | 2.5 | 0.3 |  | 32.75 | 35 |  |  |  | 38.25 | 30 |  | -15 | Positive | 0.36 | TRUE |  |  |  |  | 10 | 0.675 | 0.675 |  |  | 1 | 0 | 3 | 250 | 215 |  |  |  |  | 3.7037 | 151.1111 | VRV-GF-Common Areas | FXSQ40A
Lobbies | 70 | Group 10 | GF-065 | Lobby |  | 67.5 | 67.5 | 5 |  | 5 | 0 | 0 | 10 | 0 | 22 | <60 | 2.5 | 0.3 |  | 32.75 | 35 |  |  |  | 38.25 | 30 |  | -15 | Positive | 0.36 | TRUE |  |  |  |  | 10 | 0.675 | 0.675 |  |  | 1 | 0 | 2.9 | 250 | 215 |  |  |  |  | 3.7037 | 146.0741 | VRV-GF-Common Areas | FXSQ40A
Corridor | 71 | Group 10 | GF-066 | Circulation Area |  | 167 | 167 | 0 |  | 0 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0.3 |  | 50.1 | 55 |  |  |  | 63.75 | 50 |  |  | Positive | 0.4 | TRUE |  |  |  |  | 10 | 1.67 | 1.67 |  |  | 1 | 0 | 14.5 | 0 | -55 |  |  |  |  | 0 | 295.2096 | VRV-GF-Common Areas | 0 | `
Lobbies | 70 | Group 10 | GF-067 | Main Entrance Hall |  | 124 | 124 | 32 |  | 32 | 0 | 0 | 10 | 0 | 22 | <60 | 2.5 | 0.3 |  | 117.2 | 120 |  |  |  | 102 | 102 |  | -85 | Positive | 0.34 | TRUE |  |  |  |  | 10 | 1.24 | 1.24 |  |  | 1 | 0 | 23.9 | 0 | -120 |  |  |  |  | 0 | 655.3226 | VRV-GF-Common Areas | 0
Waiting Area | 72 | Group-1 | FF-001 | Washers Resting Area |  | 29.5 | 29.5 | 11 |  | 11 |  |  | 50 |  | 22 | <60 | 3.8 | 0.3 |  | 50.65 | 55 | -40 |  | 46.75 | 45 |  | 0 |  | Positive | 0.61 | TRUE |  |  |  |  | 10 | 0.295 | 0.295 | 4.9 | 4.9 | 1 | 4.9 | 4.9 | 383 | 328 |  |  |  |  | 12.9831 | 564.7458 | VRV-1F-01 | FXSQ80A
Laundry Room | 73 | Group-1 | FF-002 | Laundry Room | غرفة غسيل | 15 | 15 | 0 |  | 0 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 |  |  |  | 65 | 5 |  | 75 | 75 | -75 |  | Negative | 0.8 | TRUE |  |  |  |  | 10 | 0.15 | 0.15 | 6.9 | 6.6 | 1 | 6.6 | 6.6 | 533 | 533 |  |  |  |  | 35.5333 | 1496 | VRV-1F-01 | FXSQ100A
Cafeteria | 74 | Group 2 | FF-003 | Buffet | بوفية | 12.5 | 12.5 | 3 |  | 3 |  |  | 100 |  | 22 | <60 | 3.8 | 0.9 |  | 22.65 | 20 |  |  |  | 18.75 | 19 | -25 |  | Negative | 0.48 | TRUE |  |  |  |  | 10 | 0.125 | 0.125 | 0.8 | 0.8 | 1 | 0.8 | 0.8 | 150 | 130 |  |  |  |  | 12 | 217.6 | VRV-1F-01 | FXSQ20A
bathroom | 75 | Group 2 | FF-004 | Women's Rest Room | دورة مياه نساء | 33.75 | 33.75 | 5 |  | 5 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 |  | 127.5 |  | 130 | 25 | 6 | 150 | 150 | -150 |  | Negative | 0.71 | TRUE |  |  |  |  | 10 | 0.3375 | 0.3375 | 3.4 | 2.8 | 1 | 2.8 | 2.8 | 250 | 250 |  |  |  |  | 7.4074 | 282.0741 | VRV-1F-01 | FXSQ40A
bathroom | 76 | Group 3 | FF-005 | Bathroom | حمام | 8.75 | 8.75 | 1 |  | 1 |  |  | 0 |  | 22 | <60 | 0 | 0 |  | 0 | 0 | 20 | 25 | 1 | 25 | 25 | -25 |  | Negative | 0.69 | TRUE |  |  |  |  | 10 | 0.0875 | 0.0875 | 1.8 | 1.6 | 1 | 1.6 | 1.8 | 150 | 150 |  |  |  |  | 17.1429 | 699.4286 | VRV-1F-01 | FXSQ25A
Office | 77 | Group 2 | FF-006 | Maintenance Team Office | مكتب فريق الصيانة | 17.5 | 17.5 | 3 |  | 3 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 12.75 | 15 |  |  |  | 12.75 | 0 | 0 | -10 | Positive | 0.34 | TRUE |  |  |  |  | 10 | 0.175 | 0.175 | 1.6 | 1.6 | 1 | 1.6 | 1.6 | 150 | 135 |  |  |  |  | 8.5714 | 310.8571 | VRV-1F-01 | FXSQ25A
Office | 78 | Group 3 | FF-007 | General Supervisor's Secretary | سكرتير المشرف العام | 20 | 20 | 3 |  | 3 |  |  | 5 |  | 22 | <60 | 2.5 | 0.3 |  | 13.5 | 15 |  |  |  | 12.75 |  | 0 | -10 | Positive | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 | 1.7 | 1.7 | 1 | 1.7 | 1.8 | 150 | 135 |  |  |  |  | 7.5 | 306 | VRV-1F-01 | FXSQ25A
Office | 79 | Group 3 | FF-008 | General Supervisor's Office | مكتب المشرف العام | 66.56 | 66.56 | 15 |  | 15 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 57.468 | 60 | -20 |  |  | 51 |  | 0 | -20 | Positive | 0.36 | TRUE |  |  |  |  | 10 | 0.6656 | 0.6656 | 10 | 10 | 2 | 5 | 5.8 | 383 | 323 |  |  |  |  | 5.7542 | 296.274 | VRV-1F-01 | FXSQ80A
Meeting room | 80 | Group 3 | FF-009 | Meeting Room | غرفة اجتماعات | 41 | 41 | 12 |  | 12 |  |  | 50 |  | 22 | <60 | 2.5 | 0.3 |  | 42.3 | 45 |  |  |  | 38.25 |  | 0 | -30 | Positive | 0.44 | TRUE |  |  |  |  | 10 | 0.41 | 0.41 | 3.7 | 3.7 | 1 | 3.7 | 4.6 | 350 | 305 |  |  |  |  | 8.5366 | 381.4634 | VRV-1F-02 | FXSQ63A
Office | 81 | Group 3 | FF-010 | Administration Manager's Office | مكتب مدير الادراة | 46.8 | 46.8 | 13 |  | 13 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 46.54 | 45 | -20 |  |  | 38.25 |  | 0 | -10 | Positive | 0.38 | TRUE |  |  |  |  | 10 | 0.468 | 0.468 | 7.1 | 7.1 | 1 | 7.1 | 7.4 | 533 | 488 |  |  |  |  | 11.3889 | 537.6068 | VRV-1F-02 | FXSQ100A
Office | 82 | Group 4 | FF-011 | Customer Service Project Manager's Office | مكتب مدير مشروع خدمة العملاء | 20 | 20 | 3 |  | 3 |  |  | 5 |  | 22 | <60 | 2.5 | 0.3 |  | 13.5 | 15 | -10 |  |  | 12.75 | 0 | 0 |  | Positive | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 1.7 | 150 | 135 |  |  |  |  | 7.5 | 289 | VRV-1F-02 | FXSQ25A
bathroom | 83 | Group 3 | FF-012 | Bathroom | حمام | 10 | 10 | 1 |  | 1 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 |  | 0 | 0 | 20 | 25 | 1 | 25 | 25 | -25 |  | Negative | 0.6 | TRUE |  |  |  |  | 10 | 0.1 | 0.1 | 1.9 | 1.8 | 1 | 1.8 | 2.4 | 158 | 158 |  |  |  |  | 15.8 | 816 | VRV-1F-02 | FXSQ32A
Office | 84 | Group 4 | FF-013 | Customer Service Contractor's Office | مكتب مقاول خدمة العملاء | 43.5 | 43.5 | 3 |  | 3 |  |  | 5 |  | 22 | <60 | 2.5 | 0.3 |  | 20.55 | 25 | -10 |  |  | 21.25 | 0 | 0 |  | Positive | 0.41 | TRUE |  |  |  |  | 10 | 0.435 | 0.435 |  |  | 1 | 0 | 4 | 350 | 325 |  |  |  |  | 8.046 | 312.6437 | VRV-1F-02 | FXSQ63A
bathroom | 85 | Group 4 | FF-014 | Men's Rest Room | دورة مياه رجال | 30.72 | 30.72 | 6 |  | 6 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 |  | 127.5 | 0 | 135 | 25 | 6 | 150 | 150 | -150 |  | Negative | 0.59 | TRUE |  |  |  |  | 10 | 0.3072 | 0.3072 |  |  | 1 | 0 | 3.3 | 253 | 253 |  |  |  |  | 8.2357 | 365.2344 | VRV-1F-02 | FXSQ50A
Storage | 86 | Group 4 | FF-015 | Hygiene Store | مخزن النظافة | 16 | 16 | 1 |  | 1 |  |  | 2 |  | 22 | <60 | 0 | 0 |  | 0 | 0 | 20 |  |  | 0 | 25 | -25 |  | Negative | 0.38 | TRUE |  |  |  |  | 10 | 0.16 | 0.16 |  |  | 1 | 0 | 1.1 | 150 | 150 |  |  |  |  | 9.375 | 233.75 | VRV-1F-02 | FXSQ20A
Laundry Room | 87 | Group 5 | FF-016 | Laundry Room | غرفة غسيل | 14.8 | 14.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 |  |  | 0 | 60 | 5 |  | 74 | 65 | -65 |  | Negative | 0.41 | TRUE |  |  |  |  | 10 | 0.148 | 0.148 |  |  | 1 | 0 | 6.4 | 533 | 533 |  |  |  |  | 36.0135 | 1470.2703 | VRV-1F-02 | FXSQ100A
Waiting Area | 88 | Group 5 | FF-017 | Washers Resting Area | استراحة مغسلين | 29.5 | 29.5 | 11 |  | 11 |  |  | 50 |  | 22 | <60 | 3.8 | 0.3 |  | 50.65 | 55 | -40 |  |  |  |  | 0 |  | Positive | 0.61 | TRUE |  |  |  |  | 10 | 0.295 | 0.295 |  |  | 1 | 0 | 4.6 | 350 | 295 |  |  |  |  | 11.8644 | 530.1695 | VRV-1F-02 | FXSQ63A
Storage | 89 | Group 5 | FF-018 | Storage | مخزن | 8 | 8 | 0 |  | 0 | 0 | 0 | 2 | 0 | 22 | <60 | 0 | 0 |  | 0 | 0 | 20 |  |  | 0 | 25 | -25 |  | Negative | 0.75 | TRUE |  |  |  |  | 10 | 0.08 | 0.08 |  |  | 1 | 0 | 1.9 | 158 | 158 |  |  |  |  | 19.75 | 807.5 | VRV-1F-02 | FXSQ32A
Locker room | 90 | Group 5 | FF-019 | Changing Room | غرفة تغيير ملابس | 34 | 34 | 4 |  | 4 |  |  | 0 |  | 22 | <60 | 0 | 0 |  | 106.25 |  | 110 | 25 | 5 | 125 | 125 | -125 |  | Negative | 0.53 | TRUE |  |  |  |  | 10 | 0.34 | 0.34 |  |  | 1 | 0 | 3.9 | 350 | 350 |  |  |  |  | 10.2941 | 390 | VRV-1F-02 | FXSQ63A
Office | 91 | Group 5 | FF-020 | Preparation Shift Supervisor's Office | مكتب مشرف وردية التجهيز | 15.5 | 15.5 | 3 |  | 3 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 12.15 | 20 | -10 |  |  | 17 | 0 | 0 |  | Positive | 0.77 | TRUE |  |  |  |  | 10 | 0.155 | 0.155 |  |  | 1 | 0 | 2.8 | 250 | 230 |  |  |  |  | 16.129 | 614.1935 | VRV-1F-02 | FXSQ40A
Bedroom | 92 | Group 5 | FF-021 | Men's Washers Dormitory | مبيت مغسلين رجال | 40.5 | 40.5 | 3 |  | 3 |  |  | 10 |  | 22 | <60 | 2.5 | 0.3 |  | 19.65 | 25 | -10 |  |  | 21.25 | 0 | 0 |  | Positive | 0.44 | TRUE |  |  |  |  | 10 | 0.405 | 0.405 |  |  | 1 | 0 | 5.2 | 383 | 358 |  |  |  |  | 9.4568 | 436.5432 | VRV-1F-02 | FXSQ80A
Office | 93 | Group 4 | FF-022 | Cemetery Management Office | مكتب ادارة المقبرة | 20 | 20 | 3 |  | 3 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 13.5 | 15 | -10 |  |  | 12.75 | 0 | 0 |  | Positive | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 3.1 | 253 | 238 |  |  |  |  | 12.65 | 527 | VRV-1F-02 | FXSQ50A
Office | 94 | Group 4 | FF-023 | Monitoring Room | غرفة المراقبة | 20 | 20 | 3 |  | 3 |  |  | 5 |  | 22 | <60 | 2.5 | 0.3 |  | 13.5 | 15 | -10 |  |  | 12.75 | 0 | 0 |  | Positive | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 3.1 | 253 | 238 |  |  |  |  | 12.65 | 527 | VRV-1F-02 | FXSQ50A
Office | 95 | Group 4 | FF-024 | IT | IT | 20 | 20 | 3 |  | 3 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 13.5 | 15 | -10 |  |  | 12.75 | 0 | 0 |  | Positive | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 |  |  | 1 | 0 | 3.1 | 253 | 238 |  |  |  |  | 12.65 | 527 | VRV-1F-02 | FXSQ50A
Office | 96 | Group 3 | FF-025 | Operational and Maintenance Contractor Manager's Office | مكتب مدير مقاول التشغيل والصيانة | 20 | 20 | 3 |  | 3 |  |  | 5 |  | 22 | <60 | 2.5 | 0.3 |  | 13.5 | 15 |  |  |  | 12.75 |  | 0 | -10 | Positive | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 | 1.7 | 1.7 | 1 | 1.7 | 1.8 | 150 | 135 |  |  |  |  | 7.5 | 306 | VRV-1F-02 | FXSQ25A
Meeting room | 97 | Group 3 | FF-026 | Men's Training and Preparation Hall | قاعة تدريب وتجهيز رجال | 24.4 | 24.4 | 18 |  | 18 | 0 | 0 | 50 | 0 | 22 | <60 | 2.5 | 0.3 |  | 52.32 | 55 |  |  |  | 46.75 |  | 0 | -45 | Positive | 0.49 | TRUE |  |  |  |  | 10 | 0.244 | 0.244 | 5.1 | 5.1 | 1 | 5.1 | 5.8 | 383 | 328 |  |  |  |  | 15.6967 | 808.1967 | VRV-1F-02 | FXSQ80A
Office | 98 | Group 3 | FF-027 | Order Management Office | مكتب ادارة الطلبات | 287 | 287 | 24 |  | 24 |  |  | 5 |  | 22 | <60 | 2.5 | 0.3 |  | 146.1 | 150 |  |  |  | 127.5 |  |  | -75 | Positive | 0.31 | TRUE |  |  |  |  | 10 | 2.87 | 2.87 |  |  | 1 | 0 | 30.8 | 0 | -150 |  |  |  |  | 0 | 364.878 | VRV-1F-Common Areas | 0
Corridor | 99 | Group 2 | FF-028 | Corridor |  | 58 | 58 | 0 |  | 0 |  |  | 0 |  | 22 | <60 | 0 | 0.3 |  | 17.4 | 150 | -130 |  |  | 127.5 |  | 0 |  | Positive | 0.41 | TRUE |  |  |  |  | 10 | 0.58 | 0.58 |  |  | 1 | 0 | 1.7 | 150 | 0 |  |  |  |  | 2.5862 | 99.6552 | VRV-1F-Common Areas | FXSQ25A
Corridor | 100 | Group-1 | FF-029 | Corridor |  | 23.5 | 23.5 | 0 |  | 0 |  |  | 0 |  | 22 | <60 | 0 | 0.3 |  | 7.05 | 130 | -118 |  |  | 110.5 |  | 0 |  | Positive | 0.61 | TRUE |  |  |  |  | 10 | 0.235 | 0.235 |  |  | 1 | 0 | 0.8 | 150 | 20 |  |  |  |  | 6.383 | 115.7447 | VRV-1F-Common Areas | FXSQ20A
Corridor | 101 | Group 5 | FF-030 | Corridor |  | 23.5 | 23.5 | 0 |  | 0 |  |  | 0 |  | 22 | <60 | 0 | 0.3 |  | 7.05 | 145 | -130 |  |  | 123.25 | 0 | 0 |  | Positive | 0.77 | TRUE |  |  |  |  | 10 | 0.235 | 0.235 |  |  | 1 | 0 | 0.9 | 150 | 5 |  |  |  |  | 6.383 | 130.2128 | VRV-1F-Common Areas | FXSQ20A
Corridor | 102 | Group 4 | FF-031 | Corridor |  | 71.6 | 71.6 | 0 |  | 0 |  |  | 0 |  | 22 | <60 | 0 | 0.3 |  | 21.48 | 140 | -105 |  |  | 119 | 0 | 0 |  | Positive | 0.59 | TRUE |  |  |  |  | 10 | 0.716 | 0.716 |  |  | 1 | 0 | 1.8 | 150 | 10 |  |  |  |  | 2.095 | 85.4749 | VRV-1F-Common Areas | FXSQ25A
Meeting room | 103 | Group 3 | FF-033 | Women's Training and Preparation Hall | قاعة تدريب وتجهيز نساء | 24.4 | 24.4 | 18 |  | 18 | 0 | 0 | 50 | 0 | 22 | <60 | 2.5 | 0.3 |  | 52.32 | 55 |  |  |  | 46.75 |  | 0 | -45 | Positive | 0.49 | TRUE |  |  |  |  | 10 | 0.244 | 0.244 | 5.9 | 5.9 | 1 | 5.9 | 7.4 | 533 | 478 |  |  |  |  | 21.8443 | 1031.1475 | VRV-1F-01 | FXSQ100A
Office | 104 | Group 3 | FF-034 | Operations and Maintenance Contractor's Office | مكتب مقاول التشغيل والصيانة | 20 | 20 | 3 |  | 3 |  |  | 5 |  | 22 | <60 | 2.5 | 0.3 |  | 13.5 | 15 |  |  |  | 12.75 |  | 0 | -10 | Positive | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 | 1.7 | 1.7 | 1 | 1.7 | 1.8 | 150 | 135 |  |  |  |  | 7.5 | 306 | VRV-1F-01 | FXSQ25A
Office | 105 | Group 2 | FF-035 | Donations Reception Office | مكتب استقبال التبرعات | 20 | 20 | 3 |  | 3 | 0 | 0 | 5 | 0 | 22 | <60 | 2.5 | 0.3 |  | 13.5 | 15 |  |  |  | 12.75 | 0 | 0 | -10 | Positive | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 | 3.1 | 3.1 | 1 | 3.1 | 3.1 | 253 | 238 |  |  |  |  | 12.65 | 527 | VRV-1F-01 | FXSQ50A
Office | 106 | Group 2 | FF-036 | Al-Baqi' Supervisor's Office | مكتب مشرف البقيع | 20 | 20 | 3 |  | 3 |  |  | 5 |  | 22 | <60 | 2.5 | 0.3 |  | 13.5 | 15 |  |  |  | 12.75 | 0 | 0 | -10 | Positive | 0.3 | TRUE |  |  |  |  | 10 | 0.2 | 0.2 | 3.1 | 3.1 | 1 | 3.1 | 3.1 | 253 | 238 |  |  |  |  | 12.65 | 527 | VRV-1F-01 | FXSQ50A
Bedroom | 107 | Group-1 | FF-037 | Women's Washers Dormitory | مبيت مغسلين نساء | 41 | 41 | 3 |  | 3 | 0 | 0 | 10 | 0 | 22 | <60 | 2.5 | 0.3 |  | 19.8 | 25 |  |  |  | 21.25 |  | 0 |  | Positive | 0.73 | TRUE |  |  |  |  | 10 | 0.41 | 0.41 | 5.3 | 5.2 | 1 | 5.2 | 5.2 | 383 | 358 |  |  |  |  | 9.3415 | 431.2195 | VRV-1F-01 | FXSQ80A
Office | 108 | Group-1 | FF-038 | Preparation Shift Supervisor's Office | مكتب مشرف وردية التجهيز | 17.65 | 17.65 | 3 |  | 3 |  |  | 5 |  | 22 | <60 | 2.5 | 0.3 |  | 12.795 | 20 | -10 |  |  | 17 |  | 0 |  | Positive | 0.68 | TRUE |  |  |  |  | 10 | 0.1765 | 0.1765 | 2.9 | 2.9 | 1 | 2.9 | 2.9 | 250 | 230 |  |  |  |  | 14.1643 | 558.6402 | VRV-1F-01 | FXSQ40A
Locker room | 109 | Group-1 | FF-039 | Changing Room | غرفة تغيير ملابس | 30.35 | 30.35 | 4 |  | 4 | 0 | 0 | 0 | 0 | 22 | <60 | 0 | 0 |  |  |  | 80 | 25 | 5 | 100 | 100 | -100 |  | Negative | 0.79 | TRUE |  |  |  |  | 10 | 0.3035 | 0.3035 | 4.5 | 4 | 1 | 4 | 4 | 350 | 350 |  |  |  |  | 11.5321 | 448.1054 | VRV-1F-01 | FXSQ63A
Storage | 110 | Group-1 | FF-040 | Storage | مخزن | 8 | 8 | 0 |  | 0 |  |  | 2 |  | 22 | <60 | 0 | 0 |  | 0 |  | 20 |  |  |  | 25 | -25 |  | Negative | 0.75 | TRUE |  |  |  |  | 10 | 0.08 | 0.08 | 2.6 | 2.5 | 1 | 2.5 | 2.5 | 250 | 250 |  |  |  |  | 31.25 | 1062.5 | VRV-1F-01 | FXSQ40A
| Totals and Averages | [5 empty] | #REF! |  |  |  | #REF! |  |  |  | - |  | 1370 | [5 empty] | 5084 | [6 empty] | #DIV/0! | #DIV/0! | 0 KW |  |  |  | 22 KW |  |  | 79.7 | 77.8 |  |  |  | 13877 | 13877 | - | - | - | - | #REF! | #REF! | -
[30 empty] | #DIV/0! | #DIV/0! | [13 empty] | 0
[22 empty] | 51.5 |  |  |  | -1

## Data
Category | Occupancy Density as per ASHRAE | Fresh Air Requirements L/s m2 | L/s person | Exhaust Air Requirements | Lighting Density | Equipment Heat Dissipation
Storage | 2 |  |  | 7.5 | 10
Office | 5 | 0.3 | 2.5 |  | 10
bathroom |  |  |  | 25/unit | 10
Prep and Shrouding area |  |  |  |  | 10
Waiting Area | 50 | 0.3 | 3.8 |  | 10
Cafeteria | 100 | 0.9 | 3.8 |  | 10
Prayer Room | 120 | 0.3 | 2.5 |  | 10
Ablution |  |  |  | 1.25 | 10
Laundry Room | 0 |  | 0 | 5 | 10
Corridor | 0 | 0.3 | 0 | 0 | 10
Reception | 30 | 0.3 | 2.5 |  | 10
mechanical/maintenance room |  | 0.3 |  |  | 10
Meeting room | 50 | 0.3 | 2.5 |  | 10
Bedroom | 10 | 0.3 | 2.5 |  | 10
Locker room |  |  |  | 1.25 | 10
Lobbies | 10 | 0.3 | 2.5 | 0 | 10
Trash |  |  |  | 5 | 0

## Sheet2
Unit Name | Air Flow L/s | Capacity at at 24C / 17C WB SL KW
FXSQ20A | 150 | 1.5
FXSQ25A | 150 | 1.8
FXSQ32A | 158 | 2.4
FXSQ40A | 250 | 3
FXSQ50A | 253 | 3.7
FXSQ63A | 350 | 4.6
FXSQ80A | 383 | 5.8
FXSQ100A | 533 | 7.4
FXSQ125A | 600 | 9.1
FXSQ140A | 650 | 10.5