## Sheet1
Water Service Sizing as per LAPC 610.5 & 610.11 | [6 empty] | Pipe Sizing Chart |  |  |  |  | Pipe Sizing Chart as per LAPC 610.5 & 610.11
Tag | Fixture | Quantity | FU Each |  | Total FU |  | Criteria |  |  |  |  | Criteria
WC-1 | Water Closet, 1.28 GPF Tank | 73 | 5 |  | 365 |  | Friction Loss | 4.967 |  | PSI/100FT |  | Friction Loss | 4 PSI / 100ft
LAV-1 | Lavatory | 65 | 1 |  | 65 |  | Pipe Material | Copper Type L |  |  |  | Pipe Material | Copper Type L
UNRL-1 | Uniral, Flush Tank | 21 | 4 |  | 84
MP-1 | Mop Sink | 1 | 3 |  | 3 | [6 empty] | Pipe Size (in.) | Maximum WSFU
DF-1 | Drinking fountain | 10 | 0.5 |  | 5 | [7 empty] | Cold - Flush Valve | Cold - Flush Tank | Hot (max 5 ft/s)
Restaurant |  | 1 | 60 |  | 60 |  | Pipe Size | Max Flow |  | Velocity |  | 1/2" | 0 | 1 | 1
Total Fixture Units |  |  |  |  | 582 | FU | 3/8" | 1.1 | GPM | 2.5 | ft/s | 3/4" | 0 | 6 | 6
Total Water Demand as per Fixture Units versus GPM Conversion Tablke |  |  |  |  | 155 | GPM | 1/2" | 2 | GPM | 3 | ft/s | 1" | 0 | 15 | 15
Exisitng water meter size |  |  |  |  | 2" | WM | 3/4" | 6 | GPM | 4 | ft/s | 1-1/4" | 0 | 30 | 28
[7 empty] | 1" | 12.5 | GPM | 5 | ft/s | 1-1/2" | 14 | 56 | 46
Criteria | [6 empty] | 1-1/4" | 20 | GPM | 5.5 | ft/s | 2" | 95 | 205 | 119
Maximum Pressure Available at Elevation |  |  |  |  | 83 | PSI | 1-1/2" | 32.5 | GPM | 6.5 | ft/s | 2-1/2" | 329 | 455 | 245
Minimum Pressure Available at Elevation |  |  |  |  | 62 | PSI | 2" | 70 | GPM | 8 | ft/s | 3" | 666 | 719 | 406
Elevation of Highest Fixture with respect to basement |  |  |  |  | 117 | FT | [5 empty] | 3-1/2" | 1091 | 1091 | 585
[12 empty] | 4" | 1668 | 1668 | 840
Pressure Loss Calculations
Incoming Pressure |  |  |  |  | 62 | PSI
Pressure Loss Through 2" Water Meter |  |  |  |  | -11.7 | PSI
Pressure Loss Through 2" Reduced Pressure Backflow Preventer |  |  |  |  | -14 | PSI
Pressure Gain due to Booster Pump |  |  |  |  | 45 | PSI
Pressure Loss due to Height (Elevation of Highest Fixture x 0.434) |  |  |  |  | -50.778 | PSI
Required Residual Pressure at The Farthest Fixture Group |  |  |  |  | -15 | PSI
Total Pressure Loss: |  |  |  |  | -91.478 | PSI
Available Pressure for Friction Loss (Incoming Pressure + Booster Pump Pressure Gain + Total Pressure Loss): |  |  |  |  | 15.522 | PSI
Developed Length of Water Pipe
Distance to Fathest Fixture |  |  |  |  | 250 | FT
Add 25% for Fittings |  |  |  |  | 62.5 | FT
Developed Length |  |  |  |  | 312.5 | FT
Allowable Friction Loss/100' = |  | (100' x Pressure Available for Friction Loss) |  | = | 4.967 | PSI/100FT
Developed Length
3" Supply Shall Be Sufficient As Per 2022 CPC Table 610.4 Water Supply and Distribution